Power Quality Analysis of a Fuel Cell Technology in a Distribution System

Gilson Paulillo1

1 Electricity Department

Institute of Tecnology for Development – LACTEC

Centro Politecnico da UFPR - Curitiba

BRAZIL

http://www.lactec.org.br

Abstract:- This paper presents a case study involving one of the main technologies of distributed generation – dg, commercially available, fuel cell, focusing the aspects related to the quality of the electric power supplied by such devices, especially harmonic and voltage imbalances. the measurements and evaluation were made in a fuel cell, PC25C, 200 kW power plants, based on phosphoric acid fuel cells, installed in the LACTEC facilities, in Curitiba, PR, BRAZIL. Finally, the work will present the main obtained conclusions, indicating the main aspects of power quality, which must be considered in the application of this device to distribution networks.

Key words: - Power Quality; Fuel Cell; Distributed Generation; Harmonics; Voltage Imbalance; Electrical Distribution Systems; Interconnection Requirements.

1   Introduction

The distributed generation - DG - is constituted in a new focus for the electric power generation. Differently of the centralized generation, that is responsible for the great majority of the energy supplied in the world, DG is characterized by not being dispatched by transmission lines and being of small load when its power is compared to the other types of electric power generation. Some authors put DG as an electric source of energy connected directly to the distribution networks in the consumer's point of common coupling [1], [2]. Authors as Dondi [1], Laurie [3] and Standard & Poor´s [4] put DG, besides the production, as storage of energy. Combined Heat and Power Plants - CHP and others are also purposes mentioned by the authors [3], [5], [6] and [7].  The reference [6], for his/her time, it defines DG as "any generation technology in small scale that supplies electric power direct to the consumer or to the transmission or distribution systems of the utility" [7]. On the other hand, the technical progresses happened in the power electronics and microprocessors allowed the interconnection of such devices to the electric net, with quality and efficiency, through the application of inverters for this end.

In the context above, this presents the preliminary results of a case study dealing with the operation of a fuel cell, 200 kW power plant, based on phosphoric acid fuel cells, installed at LACTEC facilities, in Curitiba-PR, Brazil, under the Power Quality point of the view - especially harmonic and voltage imbalance. The aim of this paper is to analyze the behavior of this device, as much as pollutant load for the system, as well as it is a sensitive load for the system power quality, in the point of common coupling between LACTEC and the local utility.

2   Project Description

In 1998 LACTEC and SIECO, an Argentinean dealer of uninterruptible power systems, stated a partnership to deploy PAFC based power plants, manufactured by UTC Fuel Cells (formerly International Fuel Cells), to Brazil. At the same time the local utility in the Paraná State (COPEL Distribuição) decided to evaluate opportunities and challenges related to the technologies for Distributed Generation. During the following two years LACTEC, SIECO and COPEL discussed the strategy for deployment of fuel cells: number of plants, possible applications, local support and commercial opportunities. The drivers for the project were the following:

- Introduction of fuel cell technology for energy generation in Brazil;

- Demonstration of fuel cells to consumers, scientific community and population;

- Evaluation of the possibilities for utilization of low-grade thermal energy;

- Experience with a small energy generator connected to the grid (breaking the paradigm of connection of local sources only at the nearest substation);

- For COPEL: to change the threats of Distributed Generation into opportunities of new business;

- For LACTEC: to create the basement of a Fuel Cell Laboratory focused on system integration, development of new applications, basic science and evaluation of new technologies;

- For SIECO: to open a new fuel cell market in Latin America.

The project was initiated with private resources and is based on three PC25C, 200 kW power plants based on phosphoric acid fuel cells. The order was done in January 2001 and the plants arrived in June, September and November 2001. The first power plant started the normal operation in August 20th 2001, the second is generating since March 2002 and the third will be installed in October 2002. The plants were installed in different sites and for different applications. The first one generates electricity for Computing Center and heat for restaurant, both located at COPEL facility. The fuel cell is the main source and operates in parallel with the grid and two previously installed diesel generators of 275 kVA each, all of the sources controlled by a 200 kVA battery based UPS system. The fuel cell heat substituted the LPG heater, but the consumption is far small than the thermal generation capacity, specified in 900,000 Btu/h. The Computing Center demands 140 kVA with 180 kVA at peak and the extra power is sent to the distribution grid.

The second plant was installed at LACTEC facility, which demands 350 kVA at peak but far less than the power plant capacity during weekends. In this way the fuel cell power plant was installed in parallel with the grid, complementing the load demand but not serving as stand by source. Energy quality and emissions are being analyzed at this site, according to the principle of a fuel cell laboratory based on a 200 kW power plant. Heat is not being used, as LACTEC has no demand for low-grade heat power.

The third power plant will be installed in Erasto Gaertner Hospital, located near LACTEC and focused on cancer diseases and that cares for children. This site needs a complete reform in the electrical and thermal installations to receive the power plant, and we expect the thermal demand for low-grade heat could improve efficiency until 85%. The project can study stationary applications of fuel cell in three different ways: in grid-connected operation and as main source of a reliable energy system for computer grade utilization, complementing the demand of a building with different loads inside and as a high efficiency grid-independent source for critical loads.

3   Fuel Cell - Lactec

The LACTEC´s fuel cell was produced by International Fuel Cell. This cell is fed by natural gas, reformed in a first stage to supply hydrogen, which also produce 200 kW of AC electric power. This fuel cell has three operation modes: grid connected, grid independent and idle. In the first case, it operates in parallel with the utility, being able, for instance, to reduce the consumption of energy of a given installation. In the second case, it operates independently of the distribution net, feeding a group of defined loads, according to the consumer's criteria. In the last one, it is ready to generate energy.

It is worth to point out that, in spite of this technology to be available commercially, the fuel cells application is still area of intense study. Subjects as the durability of the cells, interconnection issues, influence of the type of fuel used (e.g., injection of hydrogen substituting the natural gas), reliability levels, configuration of the electric net, readiness of gas, disputes for reliable energy, impact in the environment and in the market of energy and quality of the energy (main of the present paper), among others, are points of study during the evaluation of the technology for applications in distributed generation of energy.

4   Lactec’s FC Case Study

Figure 1, in the Appendix 1, presents the one-line diagram of the LACTEC´s FC facility. Measurements were done, by using ACE 2000 Power Quality Monitor, in order to verify the operation of the cell under the power quality point of view, especially, harmonics and voltage imbalance. The PQ monitor was installed at busbar 2.

Several condition were defined - 10, 20, 50, 100, 150 and 200 kW -, considering monitoring periods of 24 hours each. This is presented in Figure 6 which shows the different load steps during the monitored days. This procedure had been implemented to analyze harmonic injections of the FC, as well as its impact in the facility as well as utility network. Two measurement types were implemented:

- Measurements of Harmonic and Energy with the FC disconnected from the substation busbar;

- Measurement of Harmonic and Energy with the FC connected to the substation busbar.

- Results of the Harmonic Measurements and Energy Accomplished in Field

The results obtained from FC monitoring under operation conditions previously mentioned are presented in the next figures.

4.1   FC Disconnected (Figures 2 to 5)

Fig. 2. Voltages in the substation busbar 2.

Fig. 3. Currents in the secondary of the transformer TSA 2 at busbar 2.

Fig. 4. Voltage Total Harmonic Distortion – VTHD.

Fig. 5. Current Total Harmonic Distortion – ITHD.

4.2   FC Connected (Figures 6 to 9)

Fig. 6. Currents in the secondary of the transformer TR2 at busbar 2 during the monitored period – 8 days.

Fig. 7. Voltage Total Harmonic Distortion – VTHD.

Fig. 8. FC under 50 % of the full load - ITHD.

Fig. 9. FC under full load - ITHD.

5   Analysis of the Measurements

5.1   FC Disconnected

The results obtained considering the FC disconnected of the distribution network indicates:

- RMS Voltages – stable and balanced;

- Currents and Active Power - slightly unbalanced;

- Voltage Total Harmonic Distortion (VTHD) - it varied between 1,9 and 4,2%, for the three phases;

- Current Total Harmonic distortion (ITHD) - it varied among the phases – 23 % for the less distorted phase and 74 % for the more distorted phase;

- Power Factor - it varied between 0,8 and 0,95.

5.2   FC Connected

The monitoring results when the FC was connected with the distribution network at LACTEC facilities have indicated the following results:

- RMS Voltages - stable and balanced;

- Currents and Active Powers - they were shown more balanced for all of the generation conditions analyzed (10, 50 and 100 %);

- Voltage Total Harmonic Distortion (VTHD) - it varied between 1,9 and 6,0 % for the three phases;

- Current Total Harmonic distortion (ITHD) - it varied for each one of the FC operation conditions: for 10 %, it varied from 100 to 750 %; for 50 %, varied from 20 to 100 %; for 100 %, varied from 10 to 25 % of the nominal current;

- Power Factor – it also varied for each one of the FC conditions: for 10 %, FP varied from 0,2 to 0,7; for 50 %, varied from 0,7 to 0,95; for 100 % FP, was very close to 1,0.

6   Conclusions

For all of the operation conditions analyzed, the entrance in operation of the FC affects the levels of voltage total harmonic distortion, according the levels recommended in the most standards. In spite of the high harmonic content in current injected in facility, it was not capable to significantly distort the busbar voltages. It is worth to emphasize that this analysis is valid just for this case, and for another systems, especially that ones with smaller short circuit level, such condition becomes strongly relevant. Finally, we must ot remark that the results presented in this paper are preliminaries and this investigation is just in its beginning. In this case, faced to the unavailability of only one monitoring device, the results are not totally conclusive. In this way, the authors recommend that, for better results, the procedure be repeated, being used, at least and simultaneously, 2 monitoring devices: one connected in the FC output and the other in the secondary of the transformer feeder. It can be interesting also to install a third equipment close to the other loads, in order to evaluate the harmonic contribution of the same ones in the system in study.

References:

- Dondi, P. et al, “Network integration of distributed power generation”, Journal of Power Sources 106 (2002) 1-9  [DG All sci- 00 –02 – 03 –78].

- Greene N. Hammerschlag, R., “Small and Clean is Beautiful: Exploring Small and Clean Is Beautiful; Exploring the Emissions of Distributed Generation and Pollution Prevention Policies”, The Electricity Journal, Volume 13, N 5, June 2000, pp. 50-60.

- Laurie, R. A., “Distributed generation: reaching the market just in time”, The Electricity Journal Elsevier Science Inc. 1040-6190. 2001.

- Standard & Poor’s Utilities & Perspectives Newsletter Special Technology Issue – January 3rd, 2000.

- Strachan, N. Dowlatabadi H., “Distributed generation and distribution utilities”, Energy Policy 30 (2002) 649-661  [DG All sci- 00 –02 – 03 –78] [DG-Energy – 98-02 04-164].

- DPCA The Distributed Power Coalition of America, 2002. Available: http://www.distributed-generation.com/dpca/what.html.

- Turkson J, Wohlgemuth, N., “Power sector reform and distributed generation in sub-Saharan Africa”, Energy Policy 29 (2001) 135-145.

Busbar 1

Busbar 2

Fig. 1. One-Line Diagram – LACTEC.

APPENDIX